# Butterfly valve, resilient-seated, double eccentric, Düker type 4510, etec enamel

# Long face-to-face length with or without bypass

# as per EN 593, as per EN 1074 part 1-2,

with DIN DVGW type examination certificate for potable water

face-to-face length as per EN 558 basic series 15 (F5)

for potable water and raw water up to 60°C

DN 300 – 600, PN 10, PN 16, PN 25

Bypass: gate valve type 4004/2004 and fittings

Standard 1/10 of the nominal diameter. Further diameters/connecting options on request.

Flange connection measures as per EN 1092

Butterfly disk with double eccentric shaft bearing in maintenance-free bearing bushes

Medium-free bearing square connection, clearance and notch free

Closed bearing eye at the butterfly disk

Shaft and shaft sealing blow-out safe, suitable for vacuum

Disk sealing made of EPDM, chambered, adjustable, easily exchangeable, sealed in both directions

Sturdy, maintenance-free slider crank mechanism, self-locking, adjusted torque curve due to toggle lever articulation, IP Code 68, mechanical position indicator,

Pressure test as per EN 12266-1, leak rate A

Body, butterfly disk and retaining ring made of EN-GJS-400-15,

Butterfly shaft stainless steel, 1.4021 (X20Cr13)

Bearing bushes bronze CC483K (Cu-Sn12-C-GC) as per EN 1982

All bolts made of stainless steel A2

Enamelled sealing seat in the body – corrosion-resistant, protected from sub-surface migration, resistant to wear

All sealing materials correspond to the requirements as per EN 682 / EN 549

All parts in contact with the medium as per KTW recommendations and DVGW worksheet W270, corresponding to UBA (German Federal Environmental Authorities) guideline

Corrosion protection:

Body, butterfly disk and retaining ring enamelled with Düker etec enamel as per DIN EN ISO 11177 (replaces DIN 51178), as per DEV guideline, tested for soil class III as per DVGW worksheet GW 9, shade cobalt blue similar to RAL 5013.

Operation:

- with hand wheel with ball knob

- with telescope stem extension set with flanged bell, with and without position indicator

- with square cap

- with electric actuator

- with pneumatic actuator

- with hydraulic actuator

- with mechanical blocking of the butterfly disc (UVV accident prevention locking)

- with locking device

- with vertical connection for ventilation

Manufacturer: 	Düker GmbH

Hauptstrasse 39-41

D-63846 Laufach

www.dueker.de

Düker butterfly valve type 4510 or equivalent

DN	PN	Qty.	Actuator type	€/pc