# Plunger valve Düker type 7015

# as per EN 1074 part 1, 2 and 5

face-to-face length as per EN 558 basic series 15

flanges as per EN 1092-2, type 21, shape B

for potable water and raw water up to 60°C

DN 150, 200, 300, PN 10, 16, 25, 40

Shut-off and control valve for pressure adjustment and flow quantity limiting,

one-part body with eye bolts, ring-shaped passage,

sealing both ways, leak tightness as per EN 1266-1 leak rate A,

optimised flow channelling, guide rails for the piston in the body made of stainless steel of superior hardness, fixed firmly in the body – without bolting or welding,

sturdy low-wear profile sealing ring on the piston, piston rotatable in case of wear

control insert seat ring

optional:

control insert slotted cylinder

control insert special version

Data for individual design (questionnaire see www.dueker.de)

Upstream pressure:	….. bar

Downstream pressure:	….. bar

Flow rate min.:	….. l/s

Flow rate max.:	….. l/s

Materials:

Body: EN-GJS-500-14

Guiding rails: stainless steel of superior hardness, highly corrosion-resistant

Piston/slotted cylinder: 1.4301

Seat ring: 1.4301

Shaft, thrust rod, gear crank: 1.4057 high-strength stainless steel

Bearing bushes: Bronze CC483K

Clamp ring: 1.4301

All parts in contact with the medium as per DVGW worksheet W270,

as well as the presently applicable UBA (German Federal Environmental Authorities) guidelines for metallic materials, plastics and elastomers.

Corrosion protection:

inside and outside epoxy powder coating as per DIN 30677-2, as per the guidelines of 
GSK Gütegemeinschaft Schwerer Korrosionsschutz (Quality Association Heavy-Duty Corrosion Protection), layer thickness min. 250 µm, colour shade blue RAL 5005

Gearbox:

sturdy, self-impeding maintenance-free slidercrank gearbox with adjustable end stop,

connection flange to the body secured against rotating with a pin,

adjusted torque curve due to toggle lever hinge,

IP Code 68, mechanical position indicator

standard position: right-hand in flow direction as per drawing 321385 pos. 1

other gearbox positions as an option

Operation:

- gear box with hand wheel

- or electric actuator

Versions:

Type: RKV 7015

DN ………	PN ………	Actuator type ………	€/pc ………